## Power estimate tool
Power Up Coalition – Guideline for temporary power application Tool to estimate power demand for superstructure works
Context :
The Power Up Coalition aims to encourage and facilitate timely electrification of construction sites for non-public works projects in Hong Kong, reduce use of diesel generator and equipment, and promote zero-emission construction sites in the long term.
Purpose of the tool:
This tool helps forecast the estimated power demand more accurately for an application for temporary electricity, especially for large projects where a temporary transformer pillar / room or supplementary battery energy storage systems could be required in order to avoid the need for diesel generators. The tool is mainly aimed at building projects e.g. large commercial or residential projects, but could be used as reference for other projects.
Instructions:
Only two pieces of information are needed for the calculation: 1) define the main construction method for your project type (either: in situ reinforced concrete (RC)#, steel structure or MiC) and; 2) estimate the number of towers/ tower cranes needed for the project.
(# For example, if a project is constructed using in situ reinforced concrete for the podium with three MiC residential towers, the main construction method should be considered as MIC.)
Please complete the green boxes:
1. Select your project type (main construction method): |  |  |  | In situ reinforced concrete |  | (Select from drop down menu)
2. Insert the quantity of tower crane(s) * for your project : |  |  |  | 1 |  | * Tip: Normally assume 1 crane per tower unless small or oversized tower footprint (typical radius of a tower crane = 40-50m)
Estimated power demand forecast:
| Tower crane | Welder | Passenger lift | Material hoist | Office | Misc * | Total Amps
In situ reinforced concrete (RC) | 200 |  | 150 | 50 | 100 | 250 | 750
Steel structure | N/A | N/A |  |  |  |  | N/A
MiC | N/A | [5 empty] | N/A
|  |  | The estimated power demand is forecast to be: | 750 | Amps | Tip: If the estimated power demand is over 800 Amps, either a temporary transformer pillar / room will be required or battery energy storage system(s) will be needed.
For reference only:
Default power demand assumptions for typical plant and equipment:
Equiment Amps | Main construction method | Tower crane | Welder | Passenger lift | Material hoist | Office | Misc * | Total Amps
1 Tower crane | In situ reinforced concrete | 200 | N/A | 150 | 50 | 100 | 250 | 750
| Steel structure | 200 | 200 |  |  |  |  | 950
| MiC | 300 | N/A |  |  |  |  | 850
For every additional tower/ crane | In situ reinforced concrete | 200 | N/A | 50 | 50 | 50 | 100 | Add 450
| Steel structure | 200 | 200 |  |  |  |  | Add 650
| MiC | 300 | N/A |  |  |  |  | 550
Misc * = Miscellaneous includes tools, pumps, lighting, WWTP etc.